## 9PX3000IRT2U
SKU | 9PX3000IRT2U
descriptionLabel | Eaton 9PX UPS, 3000 VA, 3000 W, Input: C20, Outputs: (8) C13, (2) C19, Rack/tower, 2U
General specifications
| Product Name | Eaton 9PX UPS
| Catalog Number | 9PX3000IRT2U
| UPC | 743172081384
| Product Length/Depth | 60.5 cm
| Product Height | 8.65 cm
| Product Width | 44 cm
| Product Weight | 28 kg
| Compliances | CE Marked TUV cULus Listed CSA 22.2 FCC part 15 Class B CISPR22 Class B
| Certifications | cULus Listed EAC CE ENERGY STAR certified IEC/EN 62040-1 UL 1778 IEC/EN 62040-2
Product specifications
| Special features | Double conversion topologyConstantly monitors power conditions and regulates voltage and frequencyFirst UPS in its class to provide Unity power factor (VA=W)Energy Star qualified, provides the highest efficiency level to reduce energy and cooling costsInternal bypass allows service continuity in case of UPS faultNext-generation graphical LCD displayCompatible with Virtual environments (VMware, Hyper-V, Citrix Xen, Redhat)Meter energy consumption (down to the managed outlet groups)Hot swappable batteriesAdvanced Battery Management (ABM) technology to increase battery lifetimeLong backup time with up to 4 optional EBM
| Topology | Online/Double-conversion
| Rack size | 2U
| Construction type | 482.6 mm (19 inch) device
| Color | Black/silver
| VA rating | 3000 VA
| Wattage | 3000 W
| Rack mounting kit | Yes
| Package contents | UPSInput cable(2) IEC-IEC output cablesUSB cableSerial cable(2) brackets for 19’ mounting(2) Rack-mounting kit(2) Supports for tower mountingCable locking systemSafety instructionsQuickstart guide
| Internal bypass | Yes
| Hot swap power | No
| Auto shutdown function | Yes
| Primary frequency - max | 70 Hz
| Primary frequency - min | 40 Hz
| Input connection | C20
| Input cord length | 1.8m
| Nominal frequency | 50/60 Hz
| Input frequency range | 40-70 Hz
| Input power factor | >.99
| Receptacle | (8) C13, (2) C19
| Number of Outputs C13 | 8
| Number of Outputs C19 | 2
| Output waveform | Sine wave
| Voltage | 230V
| Output nominal voltage | 230V default (200/208/220/230/240V)
| Feed type | 1
| Voltage type | AC
Runtime graph
| Battery management | ABM & Temperature compensated charging method (user selectable)Automatic battery testDeep discharge protectionAutomatic recognition of external battery units
| Battery replacement | Hot-swappable internal batteries and extended battery modules (EBMs)
| Battery rating | 12 V / 9 Ah
| Battery type | Sealed, lead-acid
| Extended battery capability | Yes
| Runtime at half load | 9.5 min
| Communication | USB port (HID compliant)Serial port (RS232)Mini terminal block for remote On/OffMini-terminal block for remote power offMini-terminal block for output relayDry contacts (3 outputs, 1 input, optocoupler, DB9)
| Expansion slots | One slot for optional communication card
| Ethernet interface | No
| Includes network card | No
| Software compatibility | Eaton Intelligent Power Manager, Eaton Intelligent Power Protector
| User interface | Multilingual graphical LCD display
| Type of interface | Other
| Potential free switch contact | Yes
| Altitude | 3000 m
| BTU Rating | Online: 614
| Noise level | <40 dB at 1 meter
| Relative humidity | 0-96% non-condensing
| Temperature range | 0° to 40°C (32° to 104°F)
| Input voltage - max | 276 V
| Input voltage - min | 100 V
| Output voltage - max | 240 V
| Output voltage - min | 200 V
| Secondary frequency - max | 60 Hz
| Secondary frequency - min | 50 Hz
| Battery quantity | 6
| Efficiency at max. load | 94
| Efficiency (eco-mode) | 98
| Input voltage range | 176-276 V (100-276 V with derating)
| Max number of battery packs | 4
| Output frequency | 50/60 Hz
| Output power factor | 1
| Output voltage range | 200/208/220/230/240 V +/- 1%
| Phase (input) | 1
| Phase (output) | 1
| Runtime at full load | 3 min
| Voltage distortion output (linear load) - max | 3
| Power consumption | 180 W
| Input Nominal Voltage | 230V default (200/208/220/230/240V)
Date | Wed Oct 21 2026